- LOAD SCHEDULE

|  |  |  | E-6 | SCALE | NTS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | PANELBOARD: PPGFa |  |  |  |  |  |  |  |  |  |  |  | THREE PHASE, 230V, 60HZ |  |  |
| BR. |  |  | LOAD DESCRIPTION |  |  | BR. CKT. LOAD IFL IN (AMPERES) | BR. CKT. CONDUCTOR | RACEWAY |  | ACB RATING |  |  |
| CKT |  | L.O | C.O |  | OTHER LOADS | VA | VOLTAGE | THREE | PHASE CURRENT | WIRE | SIZE | TYPE | SIZE DIA. |  | CONDUIT | AT |  | AF | P |
| NO. |  |  |  |  |  |  |  |  |  |  |  |  | (MM2) |  |  |  |  | (A) |  | (A) |  |  |
|  |  |  |  |  |  |  |  | PHASE | AB | CA | BA |  |  |  | (MM) |  |  |  |  |  |  |  |
| 1 |  | 112 |  |  | 55-30W Spot Light, | 3303 | 230 |  | 14.36 |  |  | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 | 2 |  |
|  |  |  |  |  | 57-29W Down Light |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 |  |  | 7 |  | 7-Convenience Outlet | 1260 | 230 |  | 5.48 |  |  | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 | 2 |  |
| 3 |  | 116 |  |  | 9-30W Spot Light, | 3373 | 230 |  |  | 14.67 |  | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 | 2 |  |
|  |  |  |  |  | 107-29W Down Light |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4 |  |  | 6 |  | 6-Convenience Outlet | 1080 | 230 |  |  | 4.7 |  | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 | 2 |  |
| 5 |  | 144 |  |  | 144-29W Down Light | 4176 | 230 |  |  |  | 18.16 | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 | 2 |  |
| 6 |  |  | 4 |  | 4-Convenience Outlet | 720 | 230 |  |  |  | 3.13 | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 | 2 |  |
| 7 |  |  | 9 |  | 9-Convenience Outlet | 1620 | 230 |  | 7.04 |  |  | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 | 2 |  |
| 8 |  |  | 3 |  | 3-Convenience Outlet | 540 | 230 |  | 2.35 |  |  | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 | 2 |  |
| 9 |  |  | 8 |  | 8-Convenience Outlet | 1440 | 230 |  |  | 6.26 |  | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 | 2 |  |
| 10 |  |  | 9 |  | 9-Convenience Outlet | 1620 | 230 |  |  | 7.04 |  | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 | 2 |  |
| 11 |  | 3 | 6 |  | 3-Convenience Outlet, 8-30W Cove | 780 | 230 |  |  |  | 3.39 | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 | 2 |  |
| 12 |  |  |  |  | SPARE | 1000 | 230 |  |  |  | 4.35 | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 | 2 |  |
| 13 |  |  |  |  | SPARE | 1000 | 230 |  | 4.35 |  |  | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 | 2 |  |
| 14 |  |  |  |  | SPARE | 1000 | 230 |  | 4.35 |  |  | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 | 2 |  |
| TOTAL CONNECTED LOAD |  |  |  |  |  | 37.93 | 32.67 | 29.03 |  |  |  |  |  |  |  |  |  |  |  |
| TOTAL DEMAND LOAD |  |  |  |  |  | 65.69 |  |  |  |  |  |  |  |  |  |  |  |  |  |

| MIN. AMPACITY OF FEEDER | USE: 3 NO. 30.0MM2 THHN |  |  |  |  | MAX. RATING OF FEEDER CIRCUIT |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CIRCUIT CONDUCTOR |  |  |  |  |  |  |  |  |  |  |  |
| (MAFCC): |  |  |  | 1-8.0MM2 THHN (GND) |  |  |  |  | OVERCURRENT PROTECTIVE DEVICE |  |  |  |  |  |
| IFL |  |  |  | 32MM DIAMETER RSC PIPE |  |  | (MROFCOPD) |  |  |  |  |  |  |  |  |  |
| = 65.69 AMPERES |  |  |  |  |  |  |  |  | MAIN CB: 100AT, 3POLE |  |  |  |  |  |  |  |  |
| PANELBOARD: MDPGF |  |  |  |  |  |  |  |  |  |  |  | THREE PHASE, 230V, 60HZ |  |
| BR. |  | LOAD DESCRIPTION |  |  | BR. CKT. LOAD IFL IN (AMPERES) | BR. CKT. CONDUCTOR | RACEWAY |  |  | ACB RATING |  |
| CKT | L.O | C.O | OTHER LOADS | VA | VOLTAGE | THREE | PHASE CURRENT |  | WIRE | SIZE | TYPE | SIZE DIA. |  | CONDUIT |  | AT |  | AF |  | P |
| NO. |  |  |  |  |  |  |  |  |  |  |  | (MM2) |  |  |  |  |  | (A) |  | (A) |  |  |
|  |  |  |  |  |  | PHASE | AB | CA |  | BA |  |  |  | (MM) |  |  |  |  |  |  |  |  |
| 1 |  |  | PPGFa | 26 168 | 230 | 65.69 |  |  |  |  | 3+1 | 30 | THHN | 32 |  | RSC |  | 100 |  | 100 |  | 3 |
| 2 |  |  | PPGFb | 31868 | 230 | 80 |  |  |  |  | 3+1 | 30 | THHN | 32 |  | RSC |  | 100 |  | 100 |  | 3 |
| 3 |  |  | PPGFc | 31868 | 230 | 80 |  |  |  |  | 3+1 | 30 | THHN | 32 |  | RSC |  | 100 |  | 100 |  | 3 |
| 4 |  |  | PPGFd | 31868 | 230 | 80 |  |  |  |  | 3+1 | 30 | THHN | 32 |  | RSC |  | 100 |  | 100 |  | 3 |
| TOTAL CONNECTED LOAD |  |  |  | 305.69 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TOTAL DEMAND LOAD |  |  |  | 305.69 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MIN. AMPACITY OF FEEDER | USE: 3 NO. 250MM2 THHN |  |  |  |  | MAX. RATING OF FEEDER CIRCUIT |  |  |  |  |  |
| CIRCUIT CONDUCTOR |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | OVERCURRENT PROTECTIVE DEVICE |  |  |  |  |
| (MAFCC): |  |  |  | 1-30MM2 THHN (GND) |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | (MROFCOPD) |  |  |  |  |  |  |  |  |  |
| IFL= 305.69 |  |  |  | 76MM DIAMETER RSC PIPE |  |  |  |  |  |  |  |  |  |  |  |  |
| = 305.69 AMPERES |  |  |  |  |  |  |  |  | MAIN CB: 400AT, 3POLE |  |  |  |  |  |  |  |  |

|  | PANELBOARD: PP2Fa |  |  |  |  |  |  |  |  |  |  | THREE PHASE, 230V, 60HZ |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| BR. |  |  |  | LOAD DESCRIPTION |  |  | BR. CKT. LOAD IFL IN (AMPERES) | BR. CKT. CONDUCTOR | RACEWAY |  | ACB RATING |  |
| CKT |  | L.O | C.O | OTHER LOADS | VA | VOLTAGE | THREE | PHASE CURRENT | WIRE | SIZE | TYPE | SIZE DIA. |  | CONDUIT | AT |  | AF |  | P |
| NO. |  |  |  |  |  |  |  |  |  |  |  | (MM2) |  |  |  |  | (A) |  | (A) |  |  |
|  |  |  |  |  |  |  | PHASE | AB | CA | BA |  |  |  | (MM) |  |  |  |  |  |  |  |
| 1 |  | 100 |  | 100-29W Down Light | 2900 | 230 |  | 12.61 |  |  | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 |  | 2 |
| 2 |  |  | 5 | 5-Convenience Outlet | 900 | 230 |  | 3.91 |  |  | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 |  | 2 |
| 3 |  | 92 |  | 92-29W Down Light | 2668 | 230 |  |  | 11.6 |  | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 |  | 2 |
| 4 |  |  | 5 | 5-Convenience Outlet | 900 | 230 |  |  | 3.91 |  | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 |  | 2 |
| 5 |  | 112 |  | 112-29W Down Light | 3248 | 230 |  |  |  | 14.12 | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 |  | 2 |
| 6 |  |  | 7 | 7-Convenience Outlet | 1260 | 230 |  |  |  | 5.48 | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 |  | 2 |
| 7 |  |  | 5 | 5-Convenience Outlet | 900 | 230 |  | 3.91 |  |  | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 |  | 2 |
| 8 |  |  | 7 | 7-Convenience Outlet | 1260 | 230 |  | 5.48 |  |  | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 |  | 2 |
| 9 |  |  | 4 | 4-Convenience Outlet | 720 | 230 |  |  | 3.13 |  | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 |  | 2 |
| 10 |  |  | 6 | 6-Convenience Outlet | 1080 | 230 |  |  | 4.7 |  | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 |  | 2 |
| 11 |  |  |  | SPARE | 1000 | 230 |  |  |  | 4.35 | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 |  | 2 |
| 12 |  |  |  | SPARE | 1000 | 230 |  |  |  | 4.35 | 2+1 | 3.5 | THHN | 15 |  | RSC | 30 |  | 50 |  | 2 |
| TOTAL CONNECTED LOAD |  |  |  |  | 25.91 | 23.34 | 28.3 |  |  |  |  |  |  |  |  |  |  |  |
| TOTAL DEMAND LOAD |  |  |  |  | 49.02 |  |  |  |  |  |  |  |  |  |  |  |  |  |

| MIN. AMPACITY OF FEEDER | USE: 3 NO. 30.0MM2 THHN | MAX. RATING OF FEEDER CIRCUIT |
| --- | --- | --- |
| CIRCUIT CONDUCTOR |  |  |
| (MAFCC): | 1-8.0MM2 THHN (GND) | OVERCURRENT PROTECTIVE DEVICE |
| IFL | 32MM DIAMETER RSC PIPE | (MROFCOPD) |
| = 49.02 AMPERES |  | MAIN CB: 100AT, 3POLE |

|  | PANELBOARD: MDP2F |  |  |  |  |  |  |  |  |  |  |  |  | THREE PHASE, 230V, 60HZ |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| BR. |  |  | LOAD DESCRIPTION |  |  | BR. CKT. LOAD IFL IN (AMPERES) | BR. CKT. CONDUCTOR | RACEWAY |  | ACB RATING |  |
| CKT |  | L.O | C.O | OTHER LOADS | VA | VOLTAGE | THREE |  | PHASE CURRENT |  | WIRE | SIZE | TYPE | SIZE DIA. |  | CONDUIT | AT |  | AF |  | P |
| NO. |  |  |  |  |  |  |  |  |  |  |  |  |  | (MM2) |  |  |  |  | (A) |  | (A) |  |  |
|  |  |  |  |  |  |  | PHASE | AB |  | CA |  | BA |  |  |  | (MM) |  |  |  |  |  |  |  |
| 1 |  |  |  | PP1Fa | 19 527 | 230 | 49.02 |  |  |  |  |  | 3+1 | 30 | THHN | 32 |  | RSC | 100 |  | 100 |  | 3 |
| 2 |  |  |  | PP1Fb | 31868 | 230 | 80 |  |  |  |  |  | 3+1 | 30 | THHN | 32 |  | RSC | 100 |  | 100 |  | 3 |
| 3 |  |  |  | PP1Fc | 31868 | 230 | 80 |  |  |  |  |  | 3+1 | 30 | THHN | 32 |  | RSC | 100 |  | 100 |  | 3 |
| 4 |  |  |  | PP1Fd | 31868 | 230 | 80 |  |  |  |  |  | 3+1 | 30 | THHN | 32 |  | RSC | 100 |  | 100 |  | 3 |
| TOTAL CONNECTED LOAD |  |  |  | 289.02 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TOTAL DEMAND LOAD |  |  |  | 289.02 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| MIN. AMPACITY OF FEEDER | USE: 3 NO. 250MM2 THHN | MAX. RATING OF FEEDER CIRCUIT |
| --- | --- | --- |
| CIRCUIT CONDUCTOR |  |  |
|  |  | OVERCURRENT PROTECTIVE DEVICE |
| (MAFCC): | 1-30MM2 THHN (GND) |  |
|  |  | (MROFCOPD) |
| IFL= 289.02 | 76MM DIAMETER RSC PIPE |  |
| = 289.02 AMPERES |  | MAIN CB: 400AT, 3POLE |

|  |  | PROJECT TITLE: | RECOMMENDING APPROVAL: | RECOMMENDING APPROVAL: | APPROVED PERMIT FOR CONSTRUCTION: | SHEET CONTENT: | REVISIONS: | SHEET NO.: |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DUTY FREE PHILIPPINES |  |  |  |  |  |  | A | 3-28-16 |  |
|  | ARCHITECT/ENGINEER | T3 MALL - LANDSIDE |  |  |  |  |  |  | DFP |
| FIESTA MALL COMPOUND, NINOY AQUINO AVENUE, |  |  |  |  |  |  |  |  |  |
| PARANAQUE CITY |  |  |  |  |  |  |  |  | E.06 |
| PTR NO.: | REG NO.: |  | ENGR. CARLOS B. LOZADA | ENGR. OCTAVIO F. LINA | MGEN. JOSE ANGEL A. HONRADO AFP (Ret) |  |  |  |  |
| ISSUED ON: | TIN: |  |  |  |  |  |  |  |  |
|  |  | LOCATION: NAIA TERMINAL 3 |  |  |  |  |  |  |  |
| ISSUED AT: |  |  | ASST. GENERAL MANAGER FOR ENGINEERING | TERMINAL MANAGER - T3 | GENERAL MANAGER |  |  |  |  |