LIGHTING FIXTURE SCHEDULE

| TYPE | DESCRIPTION |  | MANUFACTURER / CATALOG NO. |  | LAMPS |  | VOLTAGE | NOTES |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| A1 | DECORATIVE PENDANT |  |  |  | (1) CF42TT/835 |  | 277 | DIMMING |  |
|  |  |  | LIGHTOLIER 40740 PBUC |  |  |  |  |  |  |
|  | LINEAR PENDANT |  |  |  |  |  |  |  |  |  |
| A2 | INDIRECT |  | FOCAL POINT FV3S |  | (2) F54T5HO/841 |  | 277 | DIMMING |  |
|  | CONCAVE SHEILDING |  |  |  |  |  |  |  |  |  |
|  | LINEAR PENDANT |  |  |  |  |  |  |  |  |  |
| A2b | INDIRECT |  | FOCAL POINT FV3S |  | (1) F54T5HO/841 |  | 277 | DIMMING |  |
|  | CONCAVE SHEILDING |  |  |  |  |  |  |  |  |  |
|  | 4' COVE LIGHT |  |  |  |  |  |  |  |  |  |
| A3 | 95% SPECULAR ALLUMINUM REFLECTOR |  | PRUDENTIAL SC |  | (1)F32T8/830 |  | 277 | DIMMING |  |
|  | WHITE ENAMAL FINISH |  |  |  |  |  |  |  |  |  |
|  | SURFACE MTD WALLWASH |  |  |  |  |  |  |  |  |  |
| A4 | ALUMINUM REFLECTOR |  | ERCO 65043.000 |  | (1)F28T5/841 |  | 277 |  |  |  |
|  | SILVER, SATIN MATT ANODISED |  |  |  |  |  |  |  |  |  |
|  | 8" DOWNLIGHT, HORIZONTAL LAMP |  |  |  |  |  |  |  |  |  |
| B1 | DARKLIGHT REFLECTOR ALUMINUM |  | ERCO 22225.023 |  | (2) CFQ26W/G24Q/835 |  | 277 | DIMMING |  |
|  | BRIGHT ANODISED |  |  |  |  |  |  |  |  |  |
|  | LIGHTCAST WALLWASHER |  |  |  |  |  |  |  |  |  |
| B2 | DARKLIGHT REFLECTOR ALUMINUM |  | ERCO 83855.000 |  | (2) CFQ26W/G24Q/830 |  | 277 | DIMMING |  |
|  | MIRROR VAPORISED FINISH |  |  |  |  |  |  |  |  |  |
|  | 8" DOWNLIGHT, HORIZONTAL LAMP |  |  |  |  |  |  |  |  |  |
| B3 | DARKLIGHT REFLECTOR ALUMINUM |  | ERCO 22225.023 |  | (2) CFQ26W/G24Q/841 |  | 277 |  |  |  |
|  | BRIGHT ANODISED |  |  |  |  |  |  |  |  |  |
| B4 | 8" WALLWASHER |  |  |  | (1) CFQ26W/G24Q/841 |  | 277 |  |  |  |
|  |  |  | KURT VERSEN - P905 |  |  |  |  |  |  |  |
|  | 8" DOWNLIGHT/VERTICAL LAMP |  |  |  |  |  |  |  |  |  |
| C1 | LOW BRIGHTNESS REFLECTOR |  | ERCO - 81022.023 |  | (1)MH39W/830 |  | 277 |  |  |  |
|  | OUTDOOR |  |  |  |  |  |  |  |  |  |
|  | 8" DOWNLIGHT/VERTICAL LAMP |  |  |  |  |  |  |  |  |  |
| C2 | DARKLIGHT REFLECTOR |  | ERCO - 81029.000 |  | (1)CFQ18W/G24Q/830 |  | 277 |  |  |  |
|  | OUTDOOR |  |  |  |  |  |  |  |  |  |
| C3 | 3' BOLLARD |  | LOUIS POLLSEN - BYS |  | (1)MH100W/830 |  | 277 |  |  |  |
|  | POLE LIGHT |  |  |  |  |  |  |  |  |  |
| C4 | ASYMMETRIC INDIRECT |  | PROVIDENCE - PROV-INDA |  | (1) MH50W/830 |  | 277 |  |  |  |
|  | INDIRECT REFLECTIVE OPTICAL SYSTEM |  |  |  |  |  |  |  |  |  |
|  | OUTD00R SPOT |  |  |  |  |  |  |  |  |  |
| C5 | SPHEROLIT REFLECTOR |  |  |  |  |  |  |  |  |  |
|  | SILVER, SPECULAR ANODIZED |  | ERCO - 34028.023 |  | (1)MH39W/830 |  | 277 |  |  |  |
| D1 | SCONCE |  |  |  | (1)CFQ18W/830 |  | 277 | DIMMING |  |
|  |  |  | SPILIGHITNG P1W1016 |  |  |  |  |  |  |
| D2 | TABLE LAMP |  |  |  | (1) CFQ13W/G24Q/830 |  | 120 |  | outlet |  |
|  |  |  | CUSTOM |  |  |  |  |  |  |  |

Type:	A1

Lamp:	(1)CF42TT/835

Type:	A2

Lamp:	(2)F54T5HO/841

Type:	A2b

Lamp:	(1)F54T5HO/841

Type:	A3

Lamp:	(1)F32T8/830

Type:	A4

Lamp:	(1)F28T5/841

Type:	B1

Lamp:	(2)CF26W/835

Type:	B2

Lamp:	(2)CF26W/830

Type:	B3

Lamp:	(2)CF26W/841

Type:	B4

Lamp:	(1)CF26W/841

Type:	C1

Lamp:	(1)MH39W/830

Type:	C2

Lamp:	(1)CF18W/830

Type:	C3

Lamp:	(1)MH100W/830

Type:	C4

Lamp:	(1)MH50W/830

Type:	C5

Lamp:	(1)MH39W/830

Type:	D1

Lamp:	(1)CF18W/830

Type:	D2

Lamp:	(1)CF13W/830

D	a	y	l	i	g	h	t	i	n	g	C	o	n	t	r	o	l	s

LightSaver® LCO-203 ON/OFF Switching

| Automatic ON/OFF daylighting | Five individually programmable |
| --- | --- |
| control module | adjustments for each control channel |
|  | LCD display of light |
| Multi-level switching | level readings |

Open loop control

Pushbutton programming and automated setup

PROJECT

LOCATION/TYPE

Product

Overview

Description

Watt Stopper/Legrand’s LightSaver LCO-203 pro-vides automatic ON/OFF switching control for fluorescent and HID fixtures. It is an open loop controller providing up to three zones of control from a single photocell.

Operation

The LCO controller is part of a system that includes the LS-290C photocell and the BT-203 Power Pack. Each of the LCO controller’s three channels connects directly with its own dedicated relay in the power pack. The photocell measures daylight and transmits these data to the LCO con-troller. When daylight is adequate, the LCO controller switches lighting off. When daylight diminishes below the desired setpoint, the LCO controller switches lighting back on. The ON and OFF delays for each channel are individually adjustable. The LCO controller integrates with occupancy sensors as well as an optional wall switch for manual overrides.

Multiple Channel Control

Multi-channel control enables gradual, multi-level switching of electric lighting as the daylight contri-bution increases. The LCO can be used to either switch off individual rows of lamps in a luminaire or entire luminaires. This gradual reduction is likely to provide more balanced lighting while being less distracting to occupants.

Applications

Spaces such as warehouses, storage areas, atriums, lobbies, and open office areas will benefit from use of the LCO controller.

Features

www.wattstopper.com 800.879.8585

- Simplified setup and calibration

- Optional wall switch (LS-4C) provides ON/OFF control so users can adjust lighting

- Five individually adjustable parameters for each channel: ON delay, OFF delay, deadband, set-point, load shed setpoint

- Menu-driven, pushbutton programming without special tools

- Automatic internal calculation of daylight contri-bution for each channel for simplified setup

- DIN rail mounting

- Suitable for mounting in low voltage section in control panel

- California Title 24-2005 compliant

D	a	y	l	i	g	h	t	i	n	g	C	o	n	t	r	o	l	s

Specifications

System Layout & Wiring

LCO-203 Technical Information

• Class 2 low voltage device	• Load shed setpoint from 5-60 fc

• Photocell range from 3 - 6,000 footcandles	• 24VDC supply voltage provided by BT-203

• Setpoint range from 5-60 fc	• Dimensions: 3.5” x 2.81” x 2.5” (89mm x 71mm

• Programmable deadband from 10%-80%	x 64mm) LxWxD

• Adjustable ON delay from 5-60 seconds	• UL and CUL listed; five year warranty

• Adjustable OFF delay from 3-60 minutes

System Layout

Lamps (up to 3 zones)

Zone 1	Zone 2	Zone 3

BT-203 Power Pack	LightSaver®

BT-203 Power Pack

1.800.879.8585

LCO Control Module

LCO-203	LightSaver®

1.800.879.8585

LS-290C

Photocell

LS-4C Switch

Auto

I/O

• Timer

• Energy management

system

Occupancy Sensor	Control Interlock

Ordering Information

Watt Stopper/Legrand® Pub. No. 9205

LCO-203 Wiring and Settings

LS-4C Switch	LS-290C

Photocell

|  |  |  |  | Auto |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | I/O |  |  |  |  |  |  |  | 1 | 2 | 3 |  |  |
|  |  |  | Green | Black | White | Purple | GrayBrown | Red |  |  |  | A12to | A11to | A10to |  | Display |
|  |  |  | toto | to | tototo | to |  |  |  |  |  |  |  |  |
|  |  |  | B2B3 | B4 | B5B6B7 | B8 |  |  |  |  |  |  |  |  |
|  |  | A | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | A | Navigation and |
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  |  |
|  |  | B |  |  |  |  |  |  |  |  |  |  |  |  | B | selection buttons |
| BT-203 Power Pack | LightSaver® | LCD-203 |  |  |  |  |  |  |  | LightSaver® |  |
| BT-203 Power Pack |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DIN Rail |
| 1.800.879.8585 |  |  |  |  |  | 1.800.879.8585 |  |  |  |  |  |  |  |  |
|  |  |  | LCO-203 Controller |  |  |
| Not Used |  |  |  |  |  |  |  | Not Used |  |  |  |  |  |  |
|  |  | D 1 | 2 |  |  |  | 3 | 4 |  |  |  | 5 | 6 | D | D terminals: |

Line Voltage

RJ12: quick connect to BT-203

|  | Catalog No. | Description |  | Voltage | Channels |
| --- | --- | --- | --- | --- | --- |
|  |  | LCO-203 |  | ON/OFF switching control module | 24 VDC | three |
|  |  | LS-290c |  | Photocell |  |  |  |
|  |  | BT-203 |  | Power Pack |  |  |  |
|  | ON/OFF control system options: |  |  |  |
|  | Product group |  | Catalog No. | Description |  |  |
|  |  | Switch |  |  | LS-4C | Wall Switch |  |  |
|  |  | Enclosure |  |  | LS-E8 | Screw-cover enclosure 8” x 8” x 4” (203.2mm x 203.2mm x 101.6mm) |
|  |  |  |  |  | LS-E12 | Screw-cover enclosure 12” x 12” x 4” (304.8mm x 308.8mm x 101.6mm) |

EH1

WIRING PANEL SCHEDULE

| PANEL: EH1 | MAINS: MLO |  |  |  | AMPS: 400 |  |  | AIC: 25K |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| VOLTAGE: 480Y/277 | WIRES: 4 |  | PHASE: 3 |  | MOUNTING: SURFACE |  |  | LOC: MAIN ELECTRICAL ROOM |
| DESCRIPTION | P | AMP | BRANCH CIRCUIT | CIR | DESCRIPTION | P | AMP | BRANCH CIRCUIT |
| SPARE | - | - | - | 2 | LIGHTING | 1 | 20 | 3/4"C.W/2#12+1#12GRND |
| LIGHTING | 1 | 20 | 3/4"C.W/2#12+1#12GRND | 4 | LIGHTING | 1 | 20 | 3/4"C.W/2#12+1#12GRND |
| LIGHTING | 1 | 20 | 3/4"C.W/2#12+1#12GRND | 6 | LIGHTING | 1 | 20 | 3/4"C.W/2#12+1#12GRND |
| LIGHTING | 1 | 20 | 3/4"C.W/2#12+1#12GRND | 8 | LIGHTING | 1 | 20 | 3/4"C.W/2#12+1#12GRND |
| LIGHTING | 1 | 20 | 3/4"C.W/2#12+1#12GRND | 10 | LIGHTING | 1 | 20* | 3/4"C.W/2#12+1#12GRND |
| LIGHTING | 1 | 20 | 3/4"C.W/2#12+1#12GRND | 12 | SPARE | 1 | 20 | - |
| LIGHTING | 1 | 20 | 3/4"C.W/2#12+1#12GRND | 14 | SPARE | 1 | 20 | - |
| SPARE | 1 | 20 | - | 16 | SPARE | 1 | 20 | - |
| SPARE | 1 | 20 | - | 18 | SPARE | 1 | 20 | - |
| SPARE | 1 | 20 | - | 20 | SPARE | 1 | 20 | - |
| SPARE | 1 | 20 | - | 22 | SPARE | 1 | 20 | - |
| SPARE | 1 | 20 | - | 24 | SPARE | 1 | 20 | - |
| SPARE | 1 | 20 | - | 26 | SPACE | - | - | - |
| SPARE | 1 | 20 | - | 28 | SPACE | - | - | - |
| SPARE | 1 | 20 | - | 30 | SPACE | - | - | - |
| - | - | - | - | 32 | SPACE | - | - | - |
| XFMR/PANEL EL1 | 3 | 45 | 3/4"C.W/3#8+1#10GRND | 34 | SPACE | - | - | - |
| - | - | - | - | 36 | SPACE | - | - | - |
| - | 1 | - | - | 38 | SPACE | - | - | - |
| PANEL EMP | 1 | 225 | 2-1/2"C.W/3#4/0+1#4/0GRND | 40 | SPACE | - | - | - |
| - | 1 | - | - | 42 | SPACE | - | - | - |
| CONNECTED LOAD | 16731 VA | TOTAL PHASE A |  | 7750 VA |  |  |  |
| DEMAND LOAD | 20914 VA | TOTAL PHASE B |  | 4261 VA |  |  |  |
| 25% GROWTH | 26142 VA | TOTAL PHASE C |  | 4720 VA |  |  |  |

ESCHED.XLS/EH1	Page 1

HM11

WIRING PANEL SCHEDULE

|  |  | PANEL: HM11 | MAINS: MLO |  |  |  | AMPS: 100 |  |  | AIC: 25K |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | VOLTAGE: 480Y/277 | WIRES: 4 |  | PHASE: 3 |  | MOUNTING: SURFACE |  |  | LOC: MAIN ELECTRICAL ROOM |
|  | CIR | DESCRIPTION | P | AMP | BRANCH CIRCUIT | CIR | DESCRIPTION | P | AMP | BRANCH CIRCUIT |
| 1 | LIGHTING | 1 | 20 | 3/4"C.W/2#12+1#12GRND | 2 | GEN BLOCK HTR | 2 | 20 | 3/4C.W/3#12+1#12GRND |
| 3 | LIGHTING | 1 | 20 | 3/4"C.W/2#12+1#12GRND | 4 | - | - | - | - |
| 5 | LIGHTING | 1 | 20* | 3/4"C.W/2#12+1#12GRND | 6 | LIGHTING | 1 | 20* | 3/4"C.W/2#12+1#12GRND |
| 7 | SPARE | 1 | 20 | - | 8 | SPARE | 1 | 20 | - |
| 9 | SPARE | 1 | 20 | - | 10 | SPARE | 1 | 20 | - |
| 11 | SPARE | 1 | 20 | - | 12 | SPARE | 1 | 20 | - |
| 13 | SPARE | 1 | 20 | - | 14 | SPARE | 1 | 20 | - |
| 15 | SPARE | 1 | 20 | - | 16 | SPARE | 1 | 20 | - |
| 17 | SPARE | 1 | 20 | - | 18 | SPARE | 1 | 20 | - |
| 19 | SPARE | 1 | 20 | - | 20 | SPARE | 1 | 20 | - |
| 21 | SPARE | 1 | 20 | - | 22 | SPARE | 1 | 20 | - |
| 23 | SPARE | 1 | 20 | - | 24 | SPARE | 1 | 20 | - |
| 25 | SPARE | 1 | 20 | - | 26 | SPARE | 1 | 20 | - |
| 27 | SPARE | 1 | 20 | - | 28 | SPARE | 1 | 20 | - |
| 29 | SPARE | 1 | 20 | - | 30 | SPARE | 1 | 20 | - |
| 31 | SPARE | 1 | 20 | - | 32 | SPARE | 1 | 20 | - |
| 33 | SPARE | 1 | 20 | - | 34 | SPARE | 1 | 20 | - |
| 35 | SPARE | 1 | 20 | - | 36 | SPARE | 1 | 20 | - |
| 37 | SPARE | 1 | 20 | - | 38 | SPARE | 1 | 20 | - |
| 39 | SPARE | 1 | 20 | - | 40 | SPARE | 1 | 20 | - |
| 41 | SPARE | 1 | 20 | - | 42 | SPARE | 1 | 20 | - |
|  |  | CONNECTED LOAD | 8500 VA |  | TOTAL PHASE A |  | 5600 VA |  |  |  |
|  |  | DEMAND LOAD | 10625 V A | TOTAL PHASE B |  | 3900 VA |  |  |  |
|  |  | 25% GROWTH | 13282 VA | TOTAL PHASE C |  | 8500 VA |  |  |  |

ESCHED.XLS/HM11	Page 1

L1E2

WIRING PANEL SCHEDULE

|  |  | PANEL: LIE2 | MAINS: MLO |  |  | AMPS: 225 |  |  | AIC: 14K |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | VOLTAGE: 480Y/277V | WIRES: 4 | PHASE: 3 |  | MOUNTING: SURFACE |  |  | LOC: MAIN ELEC. RM |
|  | CIR | DESCRIPTION | P | AMP |  | BRANCH CIRCUIT | CIR | DESCRIPTION | P | AMP | BRANCH CIRCUIT |
|  | 1 | LIGHTING | 1 | 20 |  | 3/4"C.W/2#12+1#12GRD. | 2 | LIGHTING | 1 | 20** | 3/4"C.W/2#12+1#12GRD. |
|  | 3 | LIGHTING | 1 | 20 |  | 3/4"C.W/2#12+1#12GRD. | 4 | LIGHTING | 1 | 20** | 3/4"C.W/2#12+1#12GRD. |
|  | 5 | LIGHTING | 1 | 20 |  | 3/4"C.W/2#12+1#12GRD. | 6 | LIGHTING XFMR | 1 | 20 | 3/4"C.W/2#12+1#12GRD. |
|  | 7 | FANS | 1 | 20 |  | 3/4"C.W/2#12+1#12GRD. | 8 | LIGHTING XFMR | 1 | 20 | 3/4"C.W/2#12+1#12GRD. |
|  | 9 | LIGHTING | 1 | 20 |  | 3/4"C.W/2#12+1#12GRD. | 10 | LIGHTING | 1 | 20 | 3/4"C.W/2#12+1#12GRD. |
|  | 11 | LIGHTING | 1 | 20 |  | 3/4"C.W/2#12+1#12GRD. | 12 | LIGHTING | 1 | 20 | 3/4"C.W/2#12+1#12GRD. |
|  | 13 | LIGHTING | 1 | 20* |  | 3/4"C.W/2#12+1#12GRD. | 14 | LIGHTING | 1 | 20 | 3/4"C.W/2#12+1#12GRD. |
|  | 15 | LIGHTING | 1 | 20* |  | 3/4"C.W/2#12+1#12GRD. | 16 | LIGHTING | 1 | 20 | 3/4"C.W/2#12+1#12GRD. |
|  | 17 | OUTDOOR DOWNLIGHT | 1 | 20 |  | 3/4"C.W/2#12+1#12GRD. | 18 | OUTDOOR POLE/BOLLARD | 1 | 20 | 1.5"C.W/2#8+1#10GRD. |
|  | 19 | SPARE | 1 | 20 |  | - | 20 | SPARE | 1 | 20 | - |
|  | 21 | SPARE | 1 | 20 |  | - | 22 | SPARE | 1 | 20 | - |
|  | 23 | SPARE | 1 | 20 |  | - | 24 | SPARE | 1 | 20 | - |
|  | 25 | SPARE | 1 | 20 |  | - | 26 | SPARE | 1 | 20 | - |
|  | 27 | SPACE | 1 | - |  | - | 28 | SPACE | 1 | - | - |
|  | 29 | SPACE | 1 | - |  | - | 30 | SPACE | 1 | - | - |
|  | 31 | SPACE | 1 | - |  | - | 32 | SPACE | 1 | - | - |
|  | 33 | SPACE | 1 | - |  | - | 34 | SPACE | 1 | - | - |
|  | 35 | SPACE | 1 | - |  | - | 36 | SPACE | 1 | - | - |
|  | 37 | SPACE | 1 | - |  | - | 38 | SPACE | 1 | - | - |
|  | 39 | SPACE | 1 | - |  | - | 40 | SPACE | 1 | - | - |
|  | 41 | SPACE | 1 | - |  | - | 42 | SPACE | 1 | - | - |
|  |  | CONNECTED LOAD | 12144 VA |  | TOTAL PHASE A | 3172 VA |  |  |  |
|  |  | DEMAND LOAD | 13905 VA |  | TOTAL PHASE B | 4536 VA |  |  |  |
|  |  | 25% GROWTH | 17381 A |  | TOTAL PHASE C | 4436 VA |  |  |  |

ESCHED.XLS/L1E2	Page 1