F8943 - SPS Commissioning Check Sheet Template

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021

Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template

Document Details

This document is only valid on the day it was printed.

| Document Owner | Manager Capital Delivery |
| --- | --- |
| References | SPS Commissioning Worksheet |
|  | End to End Test Sheet |

| This document may not, in whole or part, be copied, photocopied, reproduced or translated without | P a g e | ii |
| --- | --- | --- |
| prior consent from the CEO, Unitywater. |  |  |

Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021

Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet

Template

Contents

Contents	3

General	4

Vendor Verification	5

General	5

Mechanical	5

Civil	5

Factory Acceptance Testing (FAT)	6

Electrical, Instruments and Control (E, I & C)	6

Pre-commissioning	7

Preliminaries Checklist	7

Pre-commissioning Checklist	9

General	9

Network	9

Electrical, Instruments and Control (E, I & C)	9

Mechanical	13

Wet Testing	15

Commissioning Schedule	15

General	15

Wet Well Level Sensor Checks	15

Pump Checks	15

Pump Control Checks	16

Generator Checks	18

Wet Testing Signoff	18

SAT / Performance Testing	19

SAT Schedule	19

SAT Pre-start Checks	19

Wet Well Level Sensor Checks	19

Pump Checks	19

Pump Control Checks	19

Generator Checks	21

SAT Signoff	22

| This document may not, in whole or part, be copied, photocopied, reproduced or translated without | P a g e | 3 |
| --- | --- | --- |
| prior consent from the CEO, Unitywater. |  |  |

Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021

Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template

General

In using this document, due consideration of all other relevant Unitywater Standard Drawings and Unitywater Standard Specifications should be adhered to.

| This document may not, in whole or part, be copied, photocopied, reproduced or translated without | P a g e | 4 |
| --- | --- | --- |
| prior consent from the CEO, Unitywater. |  |  |

Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021

Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template

Vendor Verification

| PROJECT TITLE: |  | FINANCE NO: |
| --- | --- | --- |
| General |  | Result / Init. / Date |
| Mechanical |  |  |
| 1. | Pump test results been reviewed and conform with applicable standards | OK |
| 2. | Flowmeter Calibration certificate received |  | OK |
| Civil |  |  |  |  |
| 3. | Check pressure test on rising main has passed |  | OK |
| 4. | Check wet-well leakage test (hydrotest) has passed |  | OK |
| CONSTRUCTOR |  |  |
| Name: |  | Position: | Signature: | Date: |
| UNITYWATER SIGNOFF |  |  |
| Name: |  | Position: | Signature: | Date: |

| This document may not, in whole or part, be copied, photocopied, reproduced or translated without | P a g e | 5 |
| --- | --- | --- |
| prior consent from the CEO, Unitywater. |  |  |

Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021

Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template

PROJECT TITLE:

Factory Acceptance Testing (FAT)

Electrical, Instruments and Control (E, I & C)

Switchboards

FINANCE NO:

Result / Init. / Date

- The switchboard manufacturer has been provided with current Unitywater Standard Switchboard Drawings (OR, if “Design and Construct”, the ‘For Construction’ drawings have been reviewed by Unitywater and provided to the switchboard manufacturer)

OK

- The switchboard manufacturer has undertaken a full point-to-point test on all switchboard wiring

OK

- The switchboard manufacturer has provided evidence of point-to-point testing in the form of marked up wiring drawings (each connection highlighted as tested)

OK

- Any changes, outcomes or additional detail resulting from FAT testing have been marked on the drawings with the highlighted test connections. Mark-ups include all available circuits, inputs, power supply voltages, labels, wire numbers, terminals etc. These marked-up drawings are labled ‘FAT’.

OK

| 5. | Cabinet and paintwork have been inspected for any visual damage | OK |
| --- | --- | --- |
| 6. | The following is as per current drawings: | OK |
|  | • | Incomer arrangements |  |
|  | • | Cable entry provisions |  |
|  | • | Interlocking provisions |  |
|  | • Incomer protection (Fault current rating) and discrimination |  |
| 7. | Switchboard rating nameplate is attached | OK |
| 8. | Switchboard Test Certificate has been checked | OK |
| 9. | Software used during FAT is available | OK |
| 10. | Any deficiencies have been recorded to a ‘FAT punchlist register’ and rectified | OK |

Instrumentation

11. Calibration certificates have been received for instruments

OK

|  | Software |  |  |
| --- | --- | --- | --- |
|  | 12. | Software for Outstation Type is loaded |  | OK |
|  | 13. | Software blocks have been fat tested (if non standard) | OK |
|  | CONSTRUCTOR |  |  |
|  | Name: |  | Position: | Signature: | Date: |
|  | UNITYWATER SIGNOFF |  |  |
|  | Name: |  | Position: | Signature: | Date: |

| This document may not, in whole or part, be copied, photocopied, reproduced or translated without | P a g e | 6 |
| --- | --- | --- |
| prior consent from the CEO, Unitywater. |  |  |

Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021

Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template

Pre-commissioning

| PROJECT TITLE: | FINANCE NO: |
| --- | --- |

|  | Preliminaries Checklist | Result / Init. / Date |
| --- | --- | --- |
| 1. | Check all commissioning personnel have been inducted to site | OK |
| 2. | Check risk assessments and SWMS have been produced for all Pre- | OK |
|  |  | commissioning and Commissioning activities |  |

- The site is safe for commisisoning works to commence. Safety requirements include:

  - Covers and grills installed and flush

  - Davit mounting points certified

  - Fall arest mounting points certified

  - Handrails, fencing, gates and chains installed correctly

  - Emergency procedures available

  - Safety signage in place (PPE, Elecricity, SWL, Danger etc.)

OK

- Check “danger electric” marker bricks are installed at ground level and painted yellow where applicable

OK

| 5. | Rising Main acceptance testing according to standard and passed | OK |
| --- | --- | --- |
| 6. | Gravity Main acceptance testing according to standard and passed | OK |
| 7. | ‘As Constructed’ survey by licenced surveyor complete | OK |

- Changes to any detail as shown on the ‘For Construction’ drawings noted on a set of ‘For Construction’ drawings and marked ‘As Constructed

OK

- Current Unitywater Standard Drawings are on site (OR, if “Design and Construct”, the ‘For Construction’ drawings have been reviewed by Unitywater)

OK

| 10. | All required civil works testing (ITPs) completed by Contracts Inspector |  | OK |
| --- | --- | --- | --- |
| 11. | Operation and Maintenence Manuals have been received for Vendor supplied |  | OK |
|  | components and the Functional Specification is available |  |  |
| 12. | Electical supply and metering available on site |  | OK |
| 13. | Pole / pillar termination method meets all requirements |  | OK |
| 14. | Check operation of all locks on switchboards |  | OK |

- Check all cable supports and check for obstructions (e.g. cables not obstructing when lifting pump)

OK

| 16. | Selected control equipment is suitable for selected pump manufacturer | OK |
| --- | --- | --- |
| 17. | Test documentation for Mechanical equipment and Instrumentation has been | OK |
|  | received. These generally include: |  |

- Factory test results

- Test compliance cetificates

- Instrument calibration certificates

- Warranty information

| This document may not, in whole or part, be copied, photocopied, reproduced or translated without | P a g e | 7 |
| --- | --- | --- |
| prior consent from the CEO, Unitywater. |  |  |

Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021

Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template

| 18. FAT completed and critical punchlist items rectified |  | OK |
| --- | --- | --- |
| CONSTRUCTOR |  |  |  |
| Name: | Position: | Signature: | Date: |
| UNITYWATER SIGNOFF |  |  |  |
| Name: | Position: | Signature: | Date: |

| This document may not, in whole or part, be copied, photocopied, reproduced or translated without | P a g e | 8 |
| --- | --- | --- |
| prior consent from the CEO, Unitywater. |  |  |

Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021

Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template

PROJECT TITLE:

Pre-commissioning Checklist

General

FINANCE NO:

Result / Init. / Date

| 1. | Check Preliminaries Checklist completed and signed off | OK |
| --- | --- | --- |
| Network |  |
| 1. | Check Commissioning Plan has been approved by Unitywater | OK |

- Advise Network Operations and Control Room of commencement of pre-commissioning acivities and proposed timing of performance and SAT testing

OK

- Check Network Operations and Control Room are ready for performance and SAT testing and appropriate resources are availbale to assist

OK

| 4. | Confirm Network Operations are aware of impact on downstream infrastructure |  | OK |
| --- | --- | --- | --- |
| 5. | Advise treatment plant operators of proposed timing of performance and SAT |  | OK |
|  | testing (fluctuating load) |  |  |
| 6. | Check sufficient water / recycled water is available for testing |  | OK |
| 7. | Ensure impacts on upstream infrastructure from changes to overflow level have |  | OK |
|  | been assessed |  |  |

Electrical, Instruments and Control (E, I & C)

Generators

|  | 1. | Check generator mains and earth cables are installed and connected | OK |
| --- | --- | --- | --- |
|  | 2. | Record the cable insulation resistance of the 3 phases |  |
|  |  |  |  | L1 | ______ MΩ |
|  |  |  |  | L2 | ______ MΩ |
|  |  |  |  | L3 | ______ MΩ |
|  | 3. | Record earth loop impedance | ______ Ω |
|  | 4. | Check point-to-point phase continuity |  |
|  |  |  |  | R to L1 | OK |
|  |  |  |  | W to L2 | OK |
|  |  |  |  | B to L3 | OK |
|  | Switchboards |  |
|  | 5. | ENSURE SWITCHBOARD IS NOT ENERGISED | OK |
|  | 6. | Check mains and earth cables are installed and connected | OK |

| This document may not, in whole or part, be copied, photocopied, reproduced or translated without | P a g e | 9 |
| --- | --- | --- |
| prior consent from the CEO, Unitywater. |  |  |

Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021

Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template

| 7. | Record the cable insulation resistance of the 3 phases |  |
| --- | --- | --- |
|  | L1 | ______ MΩ |
|  | L2 | ______ MΩ |
|  | L3 | ______ MΩ |
| 8. | Record earth loop impedance | ______ Ω |
| 9. | Check point-to-point phase continuity |  |
|  | R to L1 | OK |
|  | W to L2 | OK |
|  | B to L3 | OK |
| 10. | Check Incomer protection set as per design | OK |
| 11. | Check all CT and other links are in place | OK |
| 12. | Check correct glands have been utilised for cable entries | OK |
| 13. | Cable screens and earthing is as per design | OK |
| 14. | Ensure switchboard main Incomer is turned OFF and tagged | OK |
| 15. | Check MEN connection | OK |
| 16. | Turn on mains switch | OK |
| 17. | ACKNOWLEDGE SWITCHBOARD IS NOW ENERGISED | OK |
| 18. | Check 3 phase voltages |  |
|  | AB | _______ V |
|  | BC | _______ V |
|  | CA | _______ V |
| Lighting and GPOs |  |
| 19. | Check light circuit breaker conforms to electrical drawings | OK |
| 20. | GPO circuit breaker(s) conform to electrical drawings | OK |
| 21. | Check earth leakage circuit breaker has been tested and results are available | OK |
| 22. | Internal and external lights are connected and working | OK |
| 23. | Internal and external GPOs are connected and working | OK |

Level Transducers

- Check surge protection barriers are installed (control panel and field). Pay particular attention to earth screen terminators.

OK

- Check connection from hydrostatic level probe No.1 to the transmitter and confirm correct operation

OK

- Check connection from hydrostatic level probe No.2 to the transmitter and confirm correct operation

OK

27. Check scaling conforms to wet well design requirements

OK

| This document may not, in whole or part, be copied, photocopied, reproduced or translated without | P a g e | 10 |
| --- | --- | --- |
| prior consent from the CEO, Unitywater. |  |  |

Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021

Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template

Flowmeters

| 28. | Check calibration certificate has been received | OK |
| --- | --- | --- |
| 29. | Check mag flow head is connected to flowmeter converter | OK |
| 30. | Check correct supply voltage available at converter | OK |
| 31. | Check analogue output is correctly connected to RTU and operating correctly | OK |
| 32. | Check totaliser output is correctly connected to RTU and operating correctly | OK |
| 33. | Check mechanical (vandal) and UV protection installed on external cable | OK |

Field Devices

| 34. | Check installation of high / overflow level switch | OK |
| --- | --- | --- |
| 35. | Check calibration of all analogue signals (including flow and pressure transmitters) | OK |
| 36. | Check setting of pressure switches | OK |
| 37. | Verify level controller (hydrostatic probe) calibration | OK |

Pump Motors

- Check pump motor name plate details have been received and applied to asset management form and electrical drawings and a second plate is mounted on the switchboard pump control door

OK

| 39. | Check pump motor name plate has been applied to MCC or disconnection box | OK |
| --- | --- | --- |
| 40. | Record pump motor winding insulation resistance |  |
|  | R-W@1000V | ______ MΩ |
|  | R-B@1000V | ______ MΩ |
|  | W-B@1000V | ______ MΩ |
|  | R-E@1000V | ______ MΩ |
|  | W-E@1000V | ______ MΩ |
|  | B-E@1000V | ______ MΩ |
| 41. | Record pump motor winding resistance |  |
|  | U-U1 | ______ Ω |
|  | V–V1 | ______ Ω |
|  | W–W1 | ______ Ω |
| 42. | Check all motor protection equipment operates as specified (e.g. water in oil | OK |
|  | sensor, thermistors, vibration sensors, bearing temperatures etc.) |  |

- For variable frequiency drive (VFD), check drive settings are setup and settings recorded

OK

| 44. | For soft starter, confirm Soft Starter settings are setup and settings recorded | OK |
| --- | --- | --- |
| 45. | For direct on-line (DOL) starter, check overload settings correct and recorded on | OK |
|  | drawing |  |

46. Perform bump test to confirm correct rotation direction

OK

| This document may not, in whole or part, be copied, photocopied, reproduced or translated without | P a g e | 11 |
| --- | --- | --- |
| prior consent from the CEO, Unitywater. |  |  |

Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021

Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template

47. Tag pump motor “out of service” to indicate readiness for testing

OK

Overflow and Emergency Start Circuits

| 48. | Confirm overflow level RL | ______ m RL |
| --- | --- | --- |
| 49. | Ensure overflow level switch is set up to the correct overflow level (sufficient | OK |
|  | distance below overflow to allow for switch activation) and confirm correct |  |
|  | operation |  |
| 50. | Check installation and correct operation of emergency start circuit | OK |
| Pump Disconnection Boxes |  |
| 51. | Check incoming and outgoing cables have been secured correctly | OK |
| 52. | Check all conduits have been sealed to prevent gassing through conduits | OK |
| Radio |  |  |
| 53. | Check radio feeder & antenna installation and cable testing (antenna to radio) | OK |
|  | have been performed, and results certificate received |  |
| 54. | Check surge protection and fly lead is connected between antenna and radio | OK |
| 55. | Check Communications earthing kits and earthing are installed on feeder and | OK |
|  | Surge Diverter respectively |  |
| 56. | Record radio system information |  |
|  | Check & Verify Make & Model are correct | OK |
|  | Record Serial # | _________ |
| 57. | Check unit is powered with correct polarity and voltage 12V DC Supply | OK |
| 58. | Check radio is programmed to the correct channel | OK |
|  | Record frequency | ______MHz |
| 59. | Check radio configuration including stream id serial paramaters are set correctly | OK |
|  | for the Outstation and record | _________ |
|  |  | _________ |
|  |  | _________ |
|  |  | _________ |
| 60. | Check data radio diagnostics communication working correctly | OK |
| Remote Telemetry Units (RTU) |  |
| 61. | Check unit is powered with correct polarity and voltage DC Supply(ies) | OK |
| 62. | Check the UPS battery is connected and charging | OK |
| 63. | Check communication is working | OK |

64. Check I/O is operational and conforms with current drawings

OK

| This document may not, in whole or part, be copied, photocopied, reproduced or translated without | P a g e | 12 |
| --- | --- | --- |
| prior consent from the CEO, Unitywater. |  |  |

Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021

Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template

Control System

| 65. | Record type of control system installed (i.e. SCADAPack, MultiSmart, MT2-PC) | _________ |
| --- | --- | --- |
| 66. | Record controller information |  |
|  | Manufacturer | _________ |
|  | Model type | _________ |
|  | Serial no | _________ |
|  | Firmware rev | _________ |
|  | Software rev | _________ |

End to End Testing

| 67. | Notify control room of impending end-to-end test (minimum 5 days notice) | OK |
| --- | --- | --- |
| 68. | Check end-to-end test sheet has been reviewed and approved by control room | OK |
| 69. | Complete End-to-End Test Sheet to verify communication to SCADA | OK |
| Mechanical |  |
| General |  |
| 70. | Check layout conforms with ‘For Construction’ piping drawings | OK |

- Undertake visual examination of installation and finish of all pipework, mechanical devices, valves, fittings and pump units

OK

| 72. | Check accuracy of tagging and labelling | OK |
| --- | --- | --- |
| 73. | Check RPZD has been installed by appropriately licenced plumber | OK |
| 74. | Check functionality and accessibility of mobile crane (franna) | OK |

- Check for any debris capable of causing damage to mechanical equipment when pumps are started

OK

- Check accessibility of access covers and equipment for operational and maintenence purposes

OK

| 77. | Check equipment is guarded appropriately |  | OK |
| --- | --- | --- | --- |
| 78. | Check stairways, landings and access ladders comply with design requirements |  | OK |
| 79. | Check that all Device O&M Manuals are available |  | OK |
| 80. | Check that manufacturers’ requirements have been met (i.e. alignment, |  | OK |
|  | lubrication, preparation, priming etc.) |  |  |

- Check instrumentation nozzles are provided in accordance with design (correct side of equipment e.g. US/DS)

OK

| 82. | Check installation and operation of instrument isolation valves | OK |
| --- | --- | --- |
| 83. | Check directional requirements (i.e. pump rotation, check valve direction etc.) | OK |

- Check commissioning pressure transmitters or gauges on either side of pump are operational

OK

| This document may not, in whole or part, be copied, photocopied, reproduced or translated without | P a g e | 13 |
| --- | --- | --- |
| prior consent from the CEO, Unitywater. |  |  |

Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021

Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template

Flowmeter

| 85. | Flowmeter calibration certificate received | OK |
| --- | --- | --- |
| 86. | Check earthing straps are installed accross both flowmeter flanges, earthing rings | OK |
|  | and to earth as specified by the equipment manufacturer |  |
| Pumps |  |
| 87. | Check impeller has a free shaft | OK |
| 88. | Prime pumps with water | OK |
| 89. | Check correct pump curves are on site | OK |

Rising Main

- Check pressure test has been undertaken according to relevant standard and passed

OK

|  | 91. | Check pipework connections to UW network have been successfully completed |  | OK |
| --- | --- | --- | --- | --- |
|  | 92. | Charge the rising main and ensure air is purged |  |  | OK |
|  | CONSTRUCTOR |  |  |  |
|  | Name: |  | Position: | Signature: |  | Date: |
|  | UNITYWATER SIGNOFF |  |  |  |
|  | Name: |  | Position: | Signature: |  | Date: |

| This document may not, in whole or part, be copied, photocopied, reproduced or translated without | P a g e | 14 |
| --- | --- | --- |
| prior consent from the CEO, Unitywater. |  |  |

Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021

Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template

Wet Testing

| PROJECT TITLE: | FINANCE NO: |
| --- | --- |

|  | Commissioning Schedule | Result / Init. / Date | UW Witness |
| --- | --- | --- | --- |
|  |  |  | / Initials |
|  | General |  |  |
|  | 1. Check Pre-commissioning Checklist completed and signed off | OK |  |
|  | Level Sensor Checks |  | YES |

- Record Top of Slab RL (m) and distance from Top of Slab to each level sensor in Commissioning Worksheet

OK

- Record well diameter and total depth for volume calculations in Commissioning Worksheet

OK

- Confirm wet well level indicated by the level probe is reflective of the actual wet well level and record readings in Commissioning Worksheet

OK

- Confirm functioning of high and high high (overflow) level alarms

Note that the overflow structure may only be brought on-line once ‘As Constructed’ overflow level has been confirmed (to remain bunged off until level confirmed)

OK

Pump Checks

Motor Checks

YES

| 6. | Ensure correct parameters are set in the VFD or Soft Starter if applicable | OK |  |
| --- | --- | --- | --- |
| 7. | Start pump with discharge valve closed and ensure the pump is running | OK |  |
|  | without undue noise, vibration and temperature |  |  |
| 8. | To ensure motor load balancing, record: |  |  |
|  | Pump running amps L1 | ________A |  |
|  | Pump running amps L2 | ________A |  |
|  | Pump running amps L3 | ________A |  |
| 9. | Stop pump | OK |  |
| 10. | Complete Low Power Tuning (Danfoss VFD) and record values into | OK |  |
|  | Commissioning Worksheet |  |  |
| 11. | Repeat steps 7 to 10 for second pump/drive | OK |  |
| Fill and Bleed Rising Main |  | YES |
| 12. | Calculate volume of water required to fill rising main | OK |  |

- Ensure sufficient water in wet well to fill rising main and perform pump operation test

OK

| This document may not, in whole or part, be copied, photocopied, reproduced or translated without | P a g e | 15 |
| --- | --- | --- |
| prior consent from the CEO, Unitywater. |  |  |

Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021

Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template

| 14. | Open pump discharge valve | OK |  |
| --- | --- | --- | --- |
| 15. | Run pump and bleed air from rising main | OK |  |
| 16. | Operate pump from 35 to 50 Hz in 5 Hz increments (if VFD type), check for | OK |  |
|  | abnormal movement or vibration |  |  |
| 17. | Perform visual inspection of pump, all piping, fittings and flanged joints for | OK |  |
|  | leakage |  |  |

Pump Performance and Flowmeter Accuracy

YES

| 18. | Complete Draw Down test and verify flowmeter accuracy |  |
| --- | --- | --- |
|  |  | OK |  |
| 19. | Complete Pump Performance test including shutoff head | OK |  |
| 20. | Use Commissioning Worksheet to record and assess results | OK |  |

Pump Control Checks

Duty Pump Fault Test (2 pumps)

YES

|  |  | 21. | Select both pumps to “off” position | OK |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | 22. | Ensure assist start level > wet well level > duty start level | OK |  |  |
|  |  | 23. | Ensure pump discharge valves are open | OK |  |  |
|  |  | 24. | Confirm both drives have no faults present | OK |  |  |
|  |  | 25. | Select Pump 1 (Duty Pump) to “automatic” position | OK |  |  |
|  |  | 26. | Confirm Duty Pump running | OK |  |  |
|  |  | 27. | Select Pump 2 (Duty Assist) to “automatic” position | OK |  |  |
|  |  | 28. | Fault Duty Pump – i.e. open one c/b feeder for phase failure relay | OK |  |  |
|  |  | 29. | Confirm Duty Assist pump starts | OK |  |  |
|  |  | 30. | Stop system – both pumps to “off” position | OK |  |  |
|  |  | 31. | Select Pump 2 as Duty Pump | OK |  |  |
|  |  | 32. | Select Pump 1 as Duty Assist | OK |  |  |
|  |  | 33. | Repeat Steps 22 to 30 | OK |  |  |
|  |  | Duty / Assist Test (2 pumps) |  | YES |
|  |  | 34. | Select both pumps to “off” position | OK |  |  |
|  |  | 35. | Ensure assist start level > wet well level > duty start level | OK |  |  |
|  |  | 36. | Ensure pump discharge valves are open | OK |  |  |
|  |  | 37. | Confirm both drives have no faults present | OK |  |  |
|  |  | 38. | Select both pumps to “automatic” position | OK |  |  |
|  |  | 39. | Confirm Pump 2 (Duty Pump) running | OK |  |  |
| This document may not, in whole or part, be copied, photocopied, reproduced or translated without | P a g e | 16 |
| prior consent from the CEO, Unitywater. |  |  |

Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021

Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template

| 40. | Manually override wet well level > than assist start level | OK |  |
| --- | --- | --- | --- |
| 41. | Confirm Assist Pump started | OK |  |
| 42. | Manually override wet well level < assist stop level | OK |  |
| 43. | Confirm Duty Assist stopped | OK |  |
| 44. | Manually override wet well level < duty stop level | OK |  |
| 45. | Confirm Duty Pump stopped | OK |  |
| 46. | Select Pump 1 as Duty Pump | OK |  |
| 47. | Select Pump 2 as Duty Assist | OK |  |
| 48. | Repeat Steps 35 to 45 | OK |  |
| 49. | Select both pumps to “off” position | OK |  |
| Pump Cycling |  | YES |
| 50. | Manually override wet well level < duty stop level (pumps are stopped) | OK |  |
| 51. | Ensure wet well level > duty start level | OK |  |
| 52. | Confirm both drives have no faults present | OK |  |
| 53. | Ensure pump discharge valves are open | OK |  |
| 54. | Select both pumps to “automatic” position | OK |  |
| 55. | Record which pump is selected as Duty Pump by controller | ______ |  |
| 56. | Manually override wet well level > duty start level | OK |  |
| 57. | Confirm Duty Pump running | OK |  |
| 58. | Manually override wet well level < duty stop level | OK |  |
| 59. | Confirm Duty Pump stopped | OK |  |
| 60. | Record which pump is selected as Duty Pump by controller | ______ |  |
| 61. | Select both pumps to “off” position | OK |  |
| Emergency Start Circuit |  | YES |
| 62. | Ensure sufficient water in wet well for test | OK |  |
| 63. | Turn off the RTU | OK |  |
| 64. | Select both pumps to “automatic” position | OK |  |
| 65. | Simulate a wet well high high level (manually lowering the probe is the | OK |  |
|  | preferred method) |  |  |
| 66. | Confirm Pump 1 starts | OK |  |
| 67. | Confirm Pump 2 starts (after pump 2 start delay) | OK |  |

- Confirm both pumps stop when water level reaches the lowest probe (stop) on the start/stop three point probe

OK

| This document may not, in whole or part, be copied, photocopied, reproduced or translated without | P a g e | 17 |
| --- | --- | --- |
| prior consent from the CEO, Unitywater. |  |  |

Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021

Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template

| 69. | Select both pumps to “off” position | OK |  |
| --- | --- | --- | --- |
| 70. | Turn on the RTU | OK |  |
| Generator Checks |  | YES |
| 71. | Ensure sufficient water in wet well for test | OK |  |
| 72. | Ensure generator main switch is off | OK |  |
| 73. | Select both pumps to “off” position | OK |  |
| 74. | Connect generator and check all connections | OK |  |
| 75. | Start generator and check phase direction and voltages | OK |  |
| 76. | Select changeover switch to generator supply | OK |  |
| 77. | Close main switch and check all voltages | OK |  |
| 78. | Select Pump 1 to “automatic” and confirm correct operation | OK |  |
|  | NOTE: If sufficient water available for testing allow system to cycle confirming |  |  |
|  | complete functionality. Otherwise override wet well level to confirm pump |  |  |
|  | operation. |  |  |

- Select Pump 2 to “automatic” and confirm correct operation

Note due to portable generator size potentially both pumps may not be able to run and shall be decided on an individual site basis.

OK

|  | 80. | Select both pumps to “off” position | OK |  |
| --- | --- | --- | --- | --- |
|  | 81. | Restore mains power and disconnect generator | OK |  |

Wet Testing Signoff

CONSTRUCTOR

Name:

Position:

Signature:

Date:

UNITYWATER WITNESS

Name:

Name:

Name:

| Position: | Signature: | Date: |
| --- | --- | --- |
| Position: | Signature: | Date: |
| Position: | Signature: | Date: |

| This document may not, in whole or part, be copied, photocopied, reproduced or translated without | P a g e | 18 |
| --- | --- | --- |
| prior consent from the CEO, Unitywater. |  |  |

Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021

Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template

SAT / Performance Testing

PROJECT TITLE:

SAT Schedule

SAT Pre-start Checks

FINANCE NO:

Result / Init. / Date

| 1. | Check Wet Testing Checklist completed and signed off | OK |
| --- | --- | --- |
| 2. | Check SAT attendees are inducted to site | OK |

Level Sensor Checks

- Record Top of Slab RL (m) and distance from Top of Slab to each level sensor in Commissioning Worksheet

OK

- Record well diameter and total depth for volume calculations in Commissioning Worksheet

OK

- Confirm wet well level indicated by the level probe is reflective of the actual wet well level and record readings in Commissioning Worksheet

OK

- Confirm functioning of high and high high (overflow) level alarms

Note that the overflow structure may only be brought on-line once ‘As Constructed’ overflow level has been confirmed (to remain bunged off until level confirmed)

OK

Pump Checks

Pump Performance and Flowmeter Accuracy

| 7. | Complete Draw Down test and verify flowmeter accuracy | OK |
| --- | --- | --- |
| 8. | Complete Pump Performance test including shutoff head | OK |
| 9. | Transfer readings into Commissioning Worksheet and assess results | OK |

Pump Control Checks

Duty Pump Fault Test (2 pumps)

|  | 10. | Select both pumps to “off” position | OK |
| --- | --- | --- | --- |
|  | 11. | Ensure assist start level > wet well level > duty start level | OK |
|  | 12. | Ensure pump discharge valves are open | OK |
|  | 13. | Confirm both drives have no faults present | OK |
|  | 14. | Select Pump 1 (Duty Pump) to “automatic” position | OK |
|  | 15. | Confirm Duty Pump running | OK |

| This document may not, in whole or part, be copied, photocopied, reproduced or translated without | P a g e | 19 |
| --- | --- | --- |
| prior consent from the CEO, Unitywater. |  |  |

Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021

Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template

| 16. | Select Pump 2 (Duty Assist) to “automatic” position | OK |
| --- | --- | --- |
| 17. | Fault Duty Pump – i.e. open one c/b feeder for phase failure relay | OK |
| 18. | Confirm Duty Assist pump starts | OK |
| 19. | Stop system – both pumps to “off” position | OK |
| 20. | Select Pump 2 as Duty Pump | OK |
| 21. | Select Pump 1 as Duty Assist | OK |
| 22. | Repeat Steps 11 to 19 | OK |
| Duty / Assist Test (2 pumps) |  |
| 23. | Select both pumps to “off” position | OK |
| 24. | Ensure assist start level > wet well level > duty start level | OK |
| 25. | Ensure pump discharge valves are open | OK |
| 26. | Confirm both drives have no faults present | OK |
| 27. | Select both pumps to “automatic” position | OK |
| 28. | Confirm Pump 2 (Duty Pump) running | OK |
| 29. | Manually override wet well level > than assist start level | OK |
| 30. | Confirm Assist Pump started | OK |
| 31. | Manually override wet well level < assist stop level | OK |
| 32. | Confirm Duty Assist stopped | OK |
| 33. | Manually override wet well level < duty stop level | OK |
| 34. | Confirm Duty Pump stopped | OK |
| 35. | Select Pump 1 as Duty Pump | OK |
| 36. | Select Pump 2 as Duty Assist | OK |
| 37. | Repeat Steps 24 and 34 | OK |
| 38. | Select both pumps to “off” position | OK |
| Pump Cycling |  |
| 39. | Manually override wet well level < duty stop level (pumps are stopped) | OK |
| 40. | Ensure wet well level > duty start level | OK |
| 41. | Confirm both drives have no faults present | OK |
| 42. | Ensure pump discharge valves are open | OK |
| 43. | Select both pumps to “automatic” position | OK |
| 44. | Record which pump is selected as Duty Pump by controller | _________ |
| 45. | Manually override wet well level > duty start level | OK |

| This document may not, in whole or part, be copied, photocopied, reproduced or translated without | P a g e | 20 |
| --- | --- | --- |
| prior consent from the CEO, Unitywater. |  |  |

Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021

Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template

| 46. | Confirm Duty Pump running | OK |
| --- | --- | --- |
| 47. | Manually override wet well level < duty stop level | OK |
| 48. | Confirm Duty Pump stopped | OK |
| 49. | Record which pump is selected as Duty Pump by controller | _________ |
| 50. | Select both pumps to “off” position | OK |
| Emergency Start Circuit |  |
| 51. | Ensure sufficient water in wet well for test | OK |
| 52. | Turn off the RTU | OK |
| 53. | Select both pumps to “automatic” position | OK |
| 54. | Simulate a wet well high high level (manually lowering the probe is the preferred | OK |
|  | method) |  |
| 55. | Confirm Pump 1 starts | OK |
| 56. | Wait for several seconds (Pump 2 start delay) | OK |
| 57. | Confirm Pump 2 starts | OK |

- Confirm both pumps stop when water level reaches the lowest probe (stop) on the start/stop three point probe

OK

- Select both pumps to “off” position

- Turn on the RTU

OK

OK

Generator Checks

| 61. | Ensure sufficient water in wet well for test | OK |
| --- | --- | --- |
| 62. | Ensure generator main switch is off | OK |
| 63. | Select both pumps to “off” position | OK |
| 64. | Connect generator and check all connections | OK |
| 65. | Start generator and check phase direction and voltages | OK |
| 66. | Select changeover switch to generator supply | OK |
| 67. | Close main switch and check all voltages | OK |
| 68. | Select Pump 1 to “automatic” and confirm correct operation | OK |
|  | NOTE: If sufficient water available for testing allow system to cycle confirming |  |
|  | complete functionality. Otherwise override wet well level to confirm pump |  |
|  | operation. |  |

- Select Pump 2 to “automatic” and confirm correct operation

Note due to portable generator size potentially both pumps may not be able to run and shall be decided on an individual site basis

OK

|  |  | 70. | Select both pumps to “off” position |  | OK |
| --- | --- | --- | --- | --- | --- |
|  |  | 71. | Restore mains power and disconnect generator |  | OK |
| This document may not, in whole or part, be copied, photocopied, reproduced or translated without | P a g e | 21 |
| prior consent from the CEO, Unitywater. |  |  |

Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021

Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template

SAT Signoff

To verify completion of all SAT items to the satisfaction of Stakeholders.

CONSTRUCTOR

Name:

Position:

Signature:

Date:

UNITYWATER WITNESS (Commissioning)

Name:

Position:

Signature:

Date:

UNITYWATER WITNESS (Operations)

Name:

Position:

Signature:

Date:

UNITYWATER WITNESS (Electrical)

Name:

Position:

Signature:

Date:

UNITYWATER WITNESS (SCADA)

Name:

Position:

Signature:

Date:

UNITYWATER WITNESS (Mechanical)

Name:

Position:

Signature:

Date:

| This document may not, in whole or part, be copied, photocopied, reproduced or translated without | P a g e | 22 |
| --- | --- | --- |
| prior consent from the CEO, Unitywater. |  |  |

Printed copies are uncontrolled.